[image: image1.png]


 

AFSCONNECTOR [PVC]
FLEXIBLE DUCT CONNECTOR – PVC COATED POLYESTER
Technical Properties

	AFSCONNECTOR[PVC]
	
[image: image5.png]




	Structure
	Metal sheet + Coated fabric + Metal sheet

	METAL SHEET
	

	Metal sheet type
	Galvanized steel1

	Metal sheet thickness
	400 micron

	Metal sheet gauge2
	30 gauge

	COATED FABRIC
	

	Base fabric
	Polyester

	Coating
	PVC (both sides)
Phthalate free according to EN 14372

UV resistant

	Coated Fabric Weight3
(ASTM D3776-96)
	550 g/m2
(16.2 oz/yd2)

	Coated Fabric Thickness

(ASTM D1777-96)
	450 micron

(0.018 inch)

	Tensile strength (Warp)4
	1500 N

	Tensile strength (Weft)4
	1400 N

	Tear strength (Warp)
	250 N

	Tear strength (Weft)
	180 N

	Color
	Grey & Black

	Temperature range
	-30 (C / + 70 (C

-22 (F / + 158 (F

	Fire resistance
	Fire retardant

	LOCKING SYSTEM (Safe Seam)
	[image: image2.png]Metal Coated Fabric Metal

Metal
Coated Fabric





	Standard length
	25 m

	Packing
	Single cardboard box

	CERTIFICATES
	

	
	USA
	Intertek
	UL 723 (ASTM E84)*
FSI = 10

SDI = 400




1 : Stainless steel is available upon request (AFSCONNECTOR[PVC] INOX)
2 : Gauge express thickness and it is material dependent. Same gauge means different thicknesses for different materials. For sheet metal, thickness increases, gauge decreases.
mostly used gauges in flexible duct connectors are:

24 gauge galvanized steel = 0.701 mm = 701 micron

28 gauge galvanized steel = 0.475 mm = 475 micron

30 gauge galvanized steel = 0.399 mm = 399 micron
3 : 1 oz/yd2 = 33,9 g/m2
4 : Tensile strength: Maximum load that a material can support without fracture when being stretched, divided by the original cross-sectional area of the material (force/area)
* : UL 723: Test for surface burning characteristics of building materials

UL 723 is the Standard for Surface Burning Characteristics of Building Materials. It involves testing of building materials within a tunnel apparatus with a fire impinging on 24 ft long by 2 ft wide sample. The sample is installed horizontally with the flame impinging as if the sample were in a ceiling position. The test yields ratings for flame spread and smoke developed. This method is also commonly referred to as ASTM E84.
	[image: image3.png]


               PACKING DETAILS (40 HC / TRUCK)


	STANDARD SIZES



	Metal + Fabric + Metal

(mm x mm x mm)


	Length

(m)
	Box Dimensions

(mm x mm x mm)
	Pallet Size

(cm x cm x cm)
	Boxes/Pallet

	35 x 60 x 35
	25
	430 x 180 x 430
	100 x 110 x 205
	50

	35 x 60 x 35
	50
	500 x 180 x 500
	104 x 110 x 233
	50

	45 x 60 x 45
	25
	430 x 180 x 430
	100 x 110 x 205
	50

	45 x 60 x 45
	50
	500 x 180 x 500
	104 x 110 x 233
	50

	45 x 75 x 45
	25
	430 x 180 x 430
	100 x 110 x 205
	50

	45 x 75 x 45
	50
	500 x 180 x 500
	104 x 110 x 233
	50

	70 x 100 x 70
	25
	430 x 250 x 430
	100 x 110 x 205
	32

	70 x 100 x 70
	50
	500 x 250 x 500
	100 x 110 x 240
	34

	SPECIAL SIZES (subject to minimum order quantity)



	Metal + Fabric + Metal

(mm x mm x mm)


	Length

(m)
	Box Dimensions

(mm x mm x mm)
	Pallet Size

(cm x cm x cm)
	Boxes/Pallet

	45 x 100 x 45
	25
	430 x 180 x 430
	100 x 110 x 205
	50

	45 x 100 x 45
	50
	500 x 180 x 500
	104 x 110 x 233
	50

	45 x 150 x 45
	25
	430 x 250 x 430
	100 x 110 x 205
	34

	45 x 150 x 45
	50
	500 x 250 x 500
	100 x 110 x 240
	34

	50 x 60 x 50
	25
	430 x 180 x 430
	100 x 110 x 205
	50

	50 x 60 x 50
	50
	500 x 250 x 500
	100 x 110 x 240
	34

	50 x 150 x 50
	25
	430 x 250 x 430
	100 x 110 x 205
	32

	70 x 150 x 70
	25
	430 x 300 x 430
	100 x 110 x 205
	32

	70 x 200 x 70
	25
	430 x 300 x 430
	100 x 110 x 205
	32


Stainless Steel is available only in 45 mm and 70 mm width.
[image: image4.png]


_1584541699

