## Sayfa1
FORM NO : LAB.FRM.31 / 06.03.2015 / Rev. 0
| BİRİM : SERTİFİKASYON |  | DÖNEM: 2015 | SAYFA NO:
TEMPERATURE RESISTANCE TEST REPORT
Date | 2015-03-09
Report Code | 090315.ALU.01
Product | ALUAFS.F
Diameter | Ø127 mm
Length | 1 m
RESULTS
Time(min) | Inlet Temperature (˚C) | Outlet Temperature (˚C) | Photograph No. | Evaluation
0 | - | - | 1 | The sample was tested at an inlet temperature of 250ºC for 4 hours and photographed at the end of the test. At the end of the 4 hour test, no tears, flaps or ruptures were observed.
60 | 256 | 188
120 | 251 | 193
180 | 253 | 193
240 | 253 | 193
PHOTOGRAPHS
1
4 |  |  |  |  | 5