## Sayfa1
FORM NO : LAB.FRM.31 / 06.03.2015 / Rev. 0
|  | BİRİM : SERTİFİKASYON |  | DÖNEM: 2015 | SAYFA NO:
TEMPERATURE RESISTANCE TEST REPORT
| Date | 2015-01-29
| Report Code | 130215.EH.01.PUSI
| Product | CLIPSIMFLEKS-HT900 / CLIPAFS-HT900
| Diameter | Ø127 mm
| Length | 1 m
RESULTS
| Time(min) | Inlet Temperature (˚C) | Outlet Temperature (˚C) | Photograph No. | Evaluation
| 0 | - | - | 1 | The sample was tested at an inlet temperature of 500ºC for 4 hours and photographed hourly. At the end of the first hour, colour changes were started. At the end of the 5 hour test no tears or ruptures were observed.
| 60 | 491 | 310 | 2-3
| 120 | 487 | 314 | 4
| 180 | 502 | 317 | 5
| 240 | 506 | 320 | 6
| 300 | 503 | 320 | 7
NOTE: 500 ºC is the maximum achieved temperature by the available mechanism at AFS Labratory.
PHOTOGRAPHS
1
2 |  |  |  | 3
4 |  |  |  | 5
6 |  |  | 7