## Sayfa1
FORM NO : LAB.FRM.31 / 06.03.2015 / Rev. 0
| BİRİM : SERTİFİKASYON |  |  |  | SAYFA NO:1
TEMPERATURE RESISTANCE TEST REPORT
Date | 2015-03-23
Report Code | 230315.PEAFS.01
Product | PEAFS
Diameter | Ø127 mm
Length | 1 m
RESULTS
Time(min) | Inlet Temperature (˚C) | Outlet Temperature (˚C) | Wire Pitch (mm) | Photograph No. | Evaluation
0 | - | - | 52 | 1 | The sample was tested at an inlet temperature of 70ºC for 4 hours and photographed hourly. At the end of the 4 hour test no tears or ruptures were observed.Just a little sag is observed during test.
60 | 71 | 61 | 51 | 2
120 | 72 | 58 | 51 | 3
180 | 79 | 62 | 51 | 4
240 | 72 | 58 | 51 | 5
PHOTOGRAPHS
1
5
4
3
2