## Sayfa1
FORM NO : LAB.FRM.31 / 06.03.2015 / Rev. 0
| BİRİM : SERTİFİKASYON |  | DÖNEM: 2015 | SAYFA NO:
TEMPERATURE RESISTANCE TEST REPORT
Date | 2015-04-04
Report Code | 040415.PVCAFS.HEAVY.01
Product | PVCAFS HEAVY GREY
Diameter | Ø127 mm
Length | 1 m
RESULTS
Time(min) | Inlet Temperature (˚C) | Outlet Temperature (˚C) | Photograph No. | Evaluation
0 | - | - | 1 | The sample was tested at an inlet temperature of 80ºC for 4 hours and photographed hourly. At the end of the 4 hour test no tears or ruptures were observed.
60 | 80 | 67 | 2
120 | 79 | 63 | 3
180 | 81 | 63 | 4
240 | 81 | 64 | 5
PHOTOGRAPHS
1
2
3
4
5